## Sheet1
Request for Subcontractor Quote
Project: Smith Lake Water System Improvements Project |  | Date Quote Requested: |  |  | 2021-12-29
Well #1 Treatment Site and Backwash Line |  | Date Quote Provided:
Requested by: Ryan Biehl, Project Engineer, SMA |  | Provided by: |  |  | NECA
Item | Description | Unit | Quantity | Unit Price | Total | Notes:
1 | Mobilization and Demobilization, CIP | LS | 1 |  | 0
2 | Material Testing Allowance | LS | 1 |  | 0
3 | Site preparation and grading, including clearing, grubbing, drainage, erosion control, site restoration, and all labor and materials, CIP | LS | 1 |  | 0
4 | Well #1 and Treatment Site piping, incl. all pipe, flush lines, drains, tie-ins to existing site piping, fittings, disinfection, pressure and bacteriological testing, and appurtenances not separately listed; as well as removal or abandonment of existing site piping where called for on plans or otherwise necessary and disinfection and hydrostatic pressure testing of installed site piping, CIP. Excludes gate valves, check valve vault, 4-inch flush valve assembly, and stationed 4-inch backwash line. | LS | 1 |  | 0 | NOTE: NOT SHOWN, 4" floor drain will need to be provided in bldg, drain to daylight to south. This will be added to final drawings. Note that the backwash line alignment, and even it's penetration location in the building could be adjusted if beneficial for better routing of floor drain. NOTE: in case not already called out on drawings, specs will call for ductile fittings to have cement lining and bituminous coating exterior (NOT FBE).
5 | 4-inch buried service gate valve assembly, CIP | EA | 7 |  | 0
6 | 6-inch buried service gate valve assembly, CIP | EA | 1 |  | 0
7 | 4-inch check valve assembly in pre-cast vault, CIP | EA | 1 |  | 0
8 | 4-inch Flush Valve Assembly, CIP | EA | 1 |  | 0
9 | 4-inch C900 PVC DR18 backwash line, including all trenching, fittings, tracer wire, warning tape, above ground pipe marker posts, testing, driveway restoration, regrading to match existing conditions, site restoration, and appurtenances separately listed, CIP | LF | 765 |  | 0 | We may be able to forego testing of any kind on this discharge line. The backwash is not for potable use and also is not a sanitary concern like wastewater. If NECA has experience with this on other projects, please comment as to what, if any testing you'd recommend. Note there is no valve at end of line near discharge, so to pressure test we'd need to temporarily cap anyway.
10 | 4-inch backwash line outfall assembly, CIP. Excludes wire caged rip rap. | EA | 1 |  | 0
11 | Wire caged rip-rap at backwash outfall, CIP. | SY | 3 |  | 0 | drawing detail shows 1.5 SY as of now. I bumped to 3 SY b/c seems like the detail isn't providing enough.
12 | Treatment building foundation, interior slab, external concrete driveway and porch pads, with tie-ins and appurtenances, CIP | LS | 1 |  | 0 | Geotech study/report was completed, but needs to be updated for the site built block building. Foundation design not anticipated to change significantly. Also see Note on Item #4 above, a floor drain will need to be incorporated in floor slab (to be added to final design).
13 | Treatment building, incl. doors, hardware, floor drains, insulation, and all other structural elements and finishes not separately listed, CIP | LS | 1 |  | 0
14* | Unload, install, and tie-in packaged, skid mounted water treatment system for removal of Fe/Mn from water supply, manufactured by AdEdge, including unloading skid mounted system from delivery truck and installing within building utilizing crane and/or other equipment as necessary, initial loading of treatment media into vessels, plumbing tie-ins, fittings and appurtenances not separately listed, CIP. Excludes purchase of packaged, skid mounted system. Excludes electrical and controls tie-ins of packaged system separately listed. | LS | 1 |  | 0 | Additional sheets will be added to drawing set to provide details of treatment system. Ok for NECA to NOT price this item initially if need more info first to price out the tie in and installation cost, or make assumptions and SMA realizes price may need updating once drawings final. Skid plumning will need to connect to the 3x 4-inch floor penetrations roughly where shown, but NECA will need to provide at least 4"x3" flanged reducers with di-electric isolation kits to transition to 3" stainless plumbing on skid system. Note: SMA does have detailed submittals and shop drawings from AdEdge, however, some of them need revisions due to a change from a pre-fab steel building (that would have been provided by AdEdge with system already installed) to the skid mounted system being installed in a site built block building (items12/13). I can provide the submittals and shop drawings if NECA would like 'as is' for the treatment system. Otherwise I'll have adedge update and then incorporate in set.
15 | 8-ft tall chainlink fence assembly with 3-strand barbed wire, CIP. Includes tie-in to existing fencing where shown on drawings, and removal of existing fence as needed. | LF | 140 |  | 0
16 | 12-ft Double gate assembly (two 6-ft panels), CIP | EA | 1 |  | 0
17 | 16-ft Double gate assembly (two 8-ft panels), CIP | EA | 1
18 | 3.5-ft wide personnel gate assembly, CIP | EA | 1 |  | 0
19** | Well #1 and Water Treatment Site Electrical, incl. power supply from existing Well #1 pumphouse to Treatment Building, input/output low voltage interface between existing SCADA system at Well #1 pumphouse and Skid mounted water treatment system's PLC, and new transnet radio and cabling at Well #1 Pumphouse, CIP. | LS | 1 | By Other (Technical Electric)
20** | Water Treatment Building Electrical, including lighting, heating, ventilation, receptacles, conduits, grounding, and wiring not separately listed, CIP. | LS | 1 | By Other1 (Technical Electric)
Base Quote Total: |  |  |  |  | 0
NOTES:
This work would be completed by NECA as a Subcontractor to Stewart Brothers Drilling Company (SBDC), unless otherwise agreed. SBDC already has a contract with Navajo Nation for project that should help expedite Owner's approval for work to proceed.
SBDC will be paid for work invoiced by Subcontractor, plus a previously agreed percentage.
Prices provided here shall not include SBDC mark-up.
Prices provided here shall not include Navajo Sales Tax.
Subcontractor shall communicate directly with Engineer regarding the work items above. SBDC's role is limited to coordinating payment applications.
Coordination between Subcontractor, Engineer, Subcontractors Electrician or other Electrician, Owner, NTUA, CDEC (electric utility) and SBDC is incidental to work.
Removal or of existing infrastructure where shown on Drawings, connections to existing infrastructure, connections to new infrastructure by others, and start-up of new or rehabilitated infrastructure are incidental to work.
*Item 14: NECA does not have to provide a price for this item at this time. SMA will incorporate updated design drawings for the packaged treatment system on skid from AdEdge, at which time NECA will be asked to provide a price for the work described in this item.
*Items 19 and 20: NECA does not have to provide a price for this item at this time. Technical Electric has already provided a rough cost and scope details for Item 19. SMA will provide a detailed electrical design (by our EE subconsultant) for items 19 and 20, at which time we could revisit if it makes sense for Technical Electric to remain a sub to SBDC for this work, or to sub to NECA.